## scope
Step | Goal
Develop a process which examines each transformers kW or kVA load for the max peak
and determines if the transformer is oversized or undersived.
Determine the variables needed to make each calculation;
TransformerName or TransformerId - MDMTLA.dbo.Transformer or MDM.dbo.Transformer
PowerFactor - From Config File passed as input or stored in database table.
timeInstervalHours - block for calculating the hump and RMS (Root Mean Square)
conversion of Fairenhight to Celcius
calculate temp below 30 multiplier for allowable load matrix
calculate temp above 30 multiplier fro allowable load matrix
build allowable load table
Alter the table values to show the adjusted values
Under Rated Steps
Find the peaks for a transformer or transformers
Data to Keep
TransformerId, TransformerName, kVA Peak, Read Date of the Peak
Make sure the peak date, the Read date is the most recent date since the peak
can be the same value for multiple hours, or days.
We are interested in the most recent peak.
Get the data for 24 hours around the peak.
sqaure the kVA values
Create a flag to indicate is the kVA value is > kVARating, this will let me to find the hump or the actual load duration for the peak load if one exists
Note, it is possible to have breaks in the load duration and querying for the flag for OverDuration
Once we have this data we need to find the edges of the load duration and get the 12 hours of this data so we can calculate the RMS
Table of Results
TransformerId
TransformerName
Good to have min, max, mean, median displayed as well to tell us about the data.
kVAmaxDate
kVAmax
| kVAmin | we can go fetch the date if needed
KVAavg
| kVAmedian | sql can't do this without some heavy code work arounds
TemperatureF
TemperatureC
DateMin
DateMax
We can not use the TLAReadingHeaderID because of duplicate data, and we have to attempt to remove duplicate data.
ActualLoadPercentage
EquiliventLoadPercentage
EquivalentPostLoadingCalculation
PreConditionLoadingMax
AllowableLoadColumn
DurationHours of the Load
Results of the DurationHours and AllowableLoadColumn
How can we use the summary results to rebuild the query….
The main goal would be to show the load prife
Change to the App which runs ever day….
Check if the value we just received is higher than the max peak we already have.
And save event to re-run the process for a new Unexepected Event
Proposed Charts
System Wide Results, Date of Analysis, # of Transformers, and number of locations in total. Total kW load peak. To see the distributions.
3 Charts with counts.
Histogram of overside
Histogram of correct size
Histogram of undersized
When loading the chart, have the temperature in F and disabled, the temperature curve is a distraction
from the data we wish to review
Highlight the max peak with special dot or color to make it stand out
Max could be max over lifetime, or max in the duration we just queried.
Both should be displayed, knowing the max shown for a timeframe and knowing
the max for the life time is good to know.
Issues with current TLA App
Database contins post calculated values
kVA = kW/powerfactor
Home
Top Overrated prior 30 days.
overated in the terms we now have means the transformer is too large, and never acheives or maxes over the kVA rating
What is Age about?
Plot
Transformer Over Load History for the Last 30 Days - Loaded 120% more than 0%?????? Of time.
Plot shows Overrated on the Tool Tip, it should say over loaded, need to verify with the IEEE specification to use proper terminology
Clicking on on bar takes us to the EventReport
I clicked Feb 22nd
# Events shows 48
The data is duplicated, so we either need to de-dupe on data loads or de-dupe when pulling the data.
Also, what is an event. Code describes the events as just the count of the intervals in the day.
Maybe the event should just be when kVA > KVARating

## SampleUI-OH65568040003
Transformer OH65568040003 is over loaded.
Results
[8 empty] | TransformerId | 318
[8 empty] | TransformerIDentifier | OH65568040003
[8 empty] | TransformerName | OH65568040003
[8 empty] | LocationNumber | 100300883
[8 empty] | SubstationName | Sub 1
[8 empty] | FeederName | 1
[8 empty] | kVAmin | 10.653
[8 empty] | kVAmax | 40.426
[8 empty] | kVAavg | 25.7622
[8 empty] | kVAmaxDate | 2018-02-13 19:00
[8 empty] | DateMin | 2017-12-23 01:00
[8 empty] | DateMax | 2018-03-09
[8 empty] | kVARating | 25
[8 empty] | EquivalentContinuousPriorLoad | 21.4951 | Percent
[8 empty] | EquivalentContinuousPriorLoadIntervalCount | 12
[8 empty] | EquivalentContinuousPostLoad | 18.0631 | Percent
[8 empty] | EquivalentContinuousPostLoadIntervalCount | 12
[8 empty] | EquivalentContinuousMaxLoad | 85.9806 | Percent
[8 empty] | AmbientAvgTemperatureF | 35.1
[8 empty] | AmbientAvgTemperatureC | 1.7222
[8 empty] | TemperatureBelowThirtyMultiplier | 28.2778
ReadDate | kVAReadValue | kWValue | KVARating | kVaSqaured | OverRating | PercentLoad |  | TemperatureAboveThirtyMultiplier | 0
2018-02-13 07:00 | 15.653 | 14.088 | 25 | 245.0164 | 0 | 62.61% |  | DateMaxLoadDuration | 2018-02-14 02:00
2018-02-13 08:00 | 14.68 | 13.212 | 25 | 215.5024 | 0 | 58.72% |  | DateMinLoadDuration | 2018-02-13 19:00
2018-02-13 09:00 | 20.72 | 18.648 | 25 | 429.3184 | 0 | 82.88% |  | LoadDurationHours | 8
2018-02-13 10:00 | 22.066 | 19.86 | 25 | 486.9084 | 0 | 88.26%
2018-02-13 11:00 | 23.173 | 20.856 | 25 | 536.9879 | 0 | 92.69% |  | AllowableLoadingPercentageColumn | Ninety
2018-02-13 12:00 | 21.826 | 19.644 | 25 | 476.3743 | 0 | 87.3% |  | AllowableLoadingPercentage | 149.2778 | Percent
2018-02-13 13:00 | 23.08 | 20.772 | 25 | 532.6864 | 0 | 92.32% |  | ActualLoadingPercentage | 161.704 | Percent
2018-02-13 14:00 | 21.2 | 19.08 | 25 | 449.44 | 0 | 84.8% |  | TransformerRatingPredictedChoice | 37.5 kVA
2018-02-13 15:00 | 21.92 | 19.728 | 25 | 480.4864 | 0 | 87.68% |  | TransformerRatingPredictedLoadingPercentage | 108%
2018-02-13 16:00 | 23.506 | 21.156 | 25 | 552.532 | 0 | 94.02% |  |  |  | Percent
2018-02-13 17:00 | 23.973 | 21.576 | 25 | 574.7047 | 0 | 95.89%
2018-02-13 18:00 | 23.76 | 21.384 | 25 | 564.5376 | 0 | 95.04%
2018-02-13 19:00 | 40.426 | 36.384 | 25 | 1634.2615 | 1 | 161.7%
2018-02-13 20:00 | 38.946 | 35.052 | 25 | 1516.7909 | 1 | 155.8% |  | Allowable Loading Matrix
2018-02-13 21:00 | 39.76 | 35.784 | 25 | 1580.8576 | 1 | 159% |  | DurationHrs | Fifty | SeventyFive | Ninety
2018-02-13 22:00 | 38.6 | 34.74 | 25 | 1489.96 | 1 | 154.4% |  | 1 | 240.2778 | 224.2778 | 210.2778
2018-02-13 23:00 | 36.68 | 33.012 | 25 | 1345.4224 | 1 | 146.7% |  | 2 | 207.2778 | 196.2778 | 185.2778
2018-02-14 | 34.84 | 31.356 | 25 | 1213.8256 | 1 | 139.4% | 1 | 4 | 178.2778 | 172.2778 | 164.2778
2018-02-14 01:00 | 33.506 | 30.156 | 25 | 1122.652 | 1 | 134% | 2 | 6 | 162.2778 | 159.2778 | 154.2778
2018-02-14 02:00 | 32.48 | 29.232 | 25 | 1054.9504 | 1 | 129.9% | 3 | 8 | 156.2778 | 153.2778 | 149.2778
2018-02-14 03:00 | 16.626 | 14.964 | 25 | 276.4239 | 0 | 66.5% | 4 | 12 | 150.2778 | 147.2778 | 145.2778
2018-02-14 04:00 | 13.32 | 11.988 | 25 | 177.4224 | 0 | 53.28% | 5 | 16 | 145.2778 | 143.2778 | 141.2778
2018-02-14 05:00 | 14.88 | 13.392 | 25 | 221.4144 | 0 | 59.52% | 6 | 20 | 141.2778 | 139.2778 | 138.2778
2018-02-14 06:00 | 13.546 | 12.192 | 25 | 183.4941 | 0 | 54.18% | 7 | 24 | 136.2778 | 135.2778 | 135.2778
2018-02-14 07:00 | 14.133 | 12.72 | 25 | 199.7417 | 0 | 56.53% | 8
2018-02-14 08:00 | 11.186 | 10.068 | 25 | 125.1266 | 0 | 44.74% | 9 |  |  |  |  | TransformerId | 318
2018-02-14 09:00 | 20.453 | 18.408 | 25 | 418.3252 | 0 | 81.81% | [5 empty] | TransformerIDentifier | OH65568040003
2018-02-14 10:00 | 18.893 | 17.004 | 25 | 356.9454 | 0 | 75.57% | [5 empty] | TransformerName | OH65568040003
2018-02-14 11:00 | 22.16 | 19.944 | 25 | 491.0656 | 0 | 88.64% | [5 empty] | LocationNumber | 100300883
2018-02-14 12:00 | 20.84 | 18.756 | 25 | 434.3056 | 0 | 83.36% | [5 empty] | SubstationName | Sub 1
2018-02-14 13:00 | 20.826 | 18.744 | 25 | 433.7223 | 0 | 83.3% | [5 empty] | FeederName | 1
2018-02-14 14:00 | 24.44 | 21.996 | 25 | 597.3136 | 0 | 97.76% | [5 empty] | kVAmin | 10.653
[12 empty] | kVAmax | 40.426
[12 empty] | kVAavg | 25.7622
[12 empty] | kVAmaxDate | 43144.7917
[12 empty] | DateMin | 2017-12-23 01:00
[12 empty] | DateMax | 2018-03-09
[12 empty] | kVARating | 25
[12 empty] | EquivalentContinuousPriorLoad | 21.4951 | Percent
[12 empty] | EquivalentContinuousPriorLoadIntervalCount | 12
[12 empty] | EquivalentContinuousPostLoad | 18.0631 | Percent
[12 empty] | EquivalentContinuousPostLoadIntervalCount | 12
[12 empty] | EquivalentContinuousMaxLoad | 85.9806 | Percent
[12 empty] | AmbientAvgTemperatureF | 35.1
[12 empty] | AmbientAvgTemperatureC | 1.7222
[12 empty] | TemperatureBelowThirtyMultiplier | 28.2778
[12 empty] | TemperatureAboveThirtyMultiplier | 0
[12 empty] | DateMaxLoadDuration | 2018-02-14 02:00
[12 empty] | DateMinLoadDuration | 2018-02-13 19:00
[12 empty] | LoadDurationHours | 8
[12 empty] | AllowableLoadingPercentageColumn | Ninety
[12 empty] | AllowableLoadingPercentage | 149.2778 | Percent
[12 empty] | ActualLoadingPercentage | 161.704 | Percent
[15 empty] | TransformerRatingPredictedChoice | 37.5 kVA
[15 empty] | TransformerRatingPredictedLoadingPercentage | 107.8% | Percent
[15 empty] | TransformerRatingPredictedChoice | 50 kVA
[15 empty] | TransformerRatingPredictedLoadingPercentage | 80.85% | Percent

## Quick Summary Page
cnt | kVARating | kVARating | cnt
174 | 10 | 1 | 138
39 | 1 | 10 | 34
4 | 25 | 15 | 15
3 | 37.5 | 25 | 11
3 | 75 | 50 | 4
1 | 15 | 75 | 3
1 | 112 | 112 | 3
|  | 37.5 | 1
|  | 225 | 1

## OverSized-Example-OH65575815002
THIS TRANSFORMER IS OVERSIZED BASED ON LATEST MAX PEAK
Note, now peak ever occurs over 100%
[14 empty] | TransformerID | 389
[14 empty] | TransformerIDentifier | OH65575815002
[14 empty] | TransformerName | OH65575815002
[14 empty] | LocationNumber | 101600863
[14 empty] | SubstationName | Sub 1
[14 empty] | FeederName | 2
[14 empty] | kVAmin | 56
[14 empty] | kVAmax | 101.733
[14 empty] | kVAavg | 70.8329
[14 empty] | kVAmaxDate | 43157.7917
[14 empty] | DateMin | 43092.0417
[14 empty] | DateMax | 43174
[14 empty] | kVARating | 112
[14 empty] | EquivalentContinuousPriorLoad | 71.4114
[14 empty] | EquivalentContinuousPriorLoadIntervalCount | 12
[14 empty] | EquivalentContinuousPostLoad | 70.2457
[14 empty] | EquivalentContinuousPostLoadIntervalCount | 12
[14 empty] | EquivalentContinuousMaxLoad | 63.7602
[14 empty] | AmbientTemperatureF | 35.1
TransformerID | TransformerIDentifier | TransformerName | LocationNumber | SubstationName | FeederName | ReadDate | kVAReadValue | kWValue | KVARating | kVaSqaured | OverRating | ReadLogDate | PercentLoad | AmbientTemperatureC | 1.7222
389 | OH65575815002 | OH65575815002 | 101600863 | Sub 1 | 2 | 43157.25 | 62.133 | 55.92 | 112 | 3860.5097 | 0 | 43157 | 55.48% | TemperatureBelowThirtyMultiplier | 28.2778
389 | OH65575815002 | OH65575815002 | 101600863 | Sub 1 | 2 | 43157.2917 | 61.733 | 55.56 | 112 | 3810.9633 | 0 | 43157 | 55.12% | TemperatureAboveThirtyMultiplier | 0
389 | OH65575815002 | OH65575815002 | 101600863 | Sub 1 | 2 | 43157.3333 | 63.866 | 57.48 | 112 | 4078.866 | 0 | 43157 | 57.02% | DateMaxLoadDuration | 43157.8333
389 | OH65575815002 | OH65575815002 | 101600863 | Sub 1 | 2 | 43157.375 | 70.666 | 63.6 | 112 | 4993.6836 | 0 | 43157 | 63.09% | DateMinLoadDuration | 43157.75
389 | OH65575815002 | OH65575815002 | 101600863 | Sub 1 | 2 | 43157.4167 | 69.466 | 62.52 | 112 | 4825.5252 | 0 | 43157 | 62.02% | LoadDurationHours | 3
389 | OH65575815002 | OH65575815002 | 101600863 | Sub 1 | 2 | 43157.4583 | 60.933 | 54.84 | 112 | 3712.8305 | 0 | 43157 | 54.4% | AllowableLoadingPercentageColumn | SeventyFive
389 | OH65575815002 | OH65575815002 | 101600863 | Sub 1 | 2 | 43157.5 | 63.066 | 56.76 | 112 | 3977.3204 | 0 | 43157 | 56.31% | AllowableLoadingPercentage | 196.2778
389 | OH65575815002 | OH65575815002 | 101600863 | Sub 1 | 2 | 43157.5417 | 72.666 | 65.4 | 112 | 5280.3476 | 0 | 43157 | 64.88% | ActualLoadingPercentage | 90.833
389 | OH65575815002 | OH65575815002 | 101600863 | Sub 1 | 2 | 43157.5833 | 84.266 | 75.84 | 112 | 7100.7588 | 0 | 43157 | 75.24% | TransformerRatingPredictedChoice | 75
389 | OH65575815002 | OH65575815002 | 101600863 | Sub 1 | 2 | 43157.625 | 92.266 | 83.04 | 112 | 8513.0148 | 0 | 43157 | 82.38% | TransformerRatingPredictedLoadingPercentage | 135.644
389 | OH65575815002 | OH65575815002 | 101600863 | Sub 1 | 2 | 43157.6667 | 72 | 64.8 | 112 | 5184 | 0 | 43157 | 64.29% | CreateDate | 43173.6358
389 | OH65575815002 | OH65575815002 | 101600863 | Sub 1 | 2 | 43157.7083 | 76.533 | 68.88 | 112 | 5857.3001 | 0 | 43157 | 68.33%
389 | OH65575815002 | OH65575815002 | 101600863 | Sub 1 | 2 | 43157.75 | 76.8 | 69.12 | 112 | 5898.24 | 0 | 43157 | 68.57%
389 | OH65575815002 | OH65575815002 | 101600863 | Sub 1 | 2 | 43157.7917 | 101.733 | 91.56 | 112 | 10349.6033 | 0 | 43157 | 90.83%
389 | OH65575815002 | OH65575815002 | 101600863 | Sub 1 | 2 | 43157.8333 | 84.8 | 76.32 | 112 | 7191.04 | 0 | 43157 | 75.71%
389 | OH65575815002 | OH65575815002 | 101600863 | Sub 1 | 2 | 43157.875 | 77.466 | 69.72 | 112 | 6000.9812 | 0 | 43157 | 69.17%
389 | OH65575815002 | OH65575815002 | 101600863 | Sub 1 | 2 | 43157.9167 | 82.4 | 74.16 | 112 | 6789.76 | 0 | 43157 | 73.57%
389 | OH65575815002 | OH65575815002 | 101600863 | Sub 1 | 2 | 43157.9583 | 72 | 64.8 | 112 | 5184 | 0 | 43157 | 64.29%
389 | OH65575815002 | OH65575815002 | 101600863 | Sub 1 | 2 | 43158 | 68 | 61.2 | 112 | 4624 | 0 | 43157 | 60.71%
389 | OH65575815002 | OH65575815002 | 101600863 | Sub 1 | 2 | 43158.0417 | 66.533 | 59.88 | 112 | 4426.6401 | 0 | 43158 | 59.4%
389 | OH65575815002 | OH65575815002 | 101600863 | Sub 1 | 2 | 43158.0833 | 61.333 | 55.2 | 112 | 3761.7369 | 0 | 43158 | 54.76%
389 | OH65575815002 | OH65575815002 | 101600863 | Sub 1 | 2 | 43158.125 | 62.4 | 56.16 | 112 | 3893.76 | 0 | 43158 | 55.71%
389 | OH65575815002 | OH65575815002 | 101600863 | Sub 1 | 2 | 43158.1667 | 63.466 | 57.12 | 112 | 4027.9332 | 0 | 43158 | 56.67%
389 | OH65575815002 | OH65575815002 | 101600863 | Sub 1 | 2 | 43158.2083 | 60.266 | 54.24 | 112 | 3631.9908 | 0 | 43158 | 53.81%
389 | OH65575815002 | OH65575815002 | 101600863 | Sub 1 | 2 | 43158.25 | 61.066 | 54.96 | 112 | 3729.0564 | 0 | 43158 | 54.52%
389 | OH65575815002 | OH65575815002 | 101600863 | Sub 1 | 2 | 43158.2917 | 81.333 | 73.2 | 112 | 6615.0569 | 0 | 43158 | 72.62%
389 | OH65575815002 | OH65575815002 | 101600863 | Sub 1 | 2 | 43158.3333 | 80.8 | 72.72 | 112 | 6528.64 | 0 | 43158 | 72.14%

## 3 Durations-OH63572927003
Transformer is overloaded - math assumes one 22 hour load duration….. But it is really 3 with a break 2x a day
[14 empty] | TransformerID | 94
[14 empty] | TransformerIDentifier | OH63572927003
[14 empty] | TransformerName | OH63572927003
[14 empty] | LocationNumber | 102205203
[14 empty] | SubstationName | Sub 1
[14 empty] | FeederName | 5
[14 empty] | kVAmin | 6.84
[14 empty] | kVAmax | 62.41
[14 empty] | kVAavg | 29.8928
[14 empty] | kVAmaxDate | 43166.6667
[14 empty] | DateMin | 43092.0417
[14 empty] | DateMax | 43169
[14 empty] | kVARating | 25
[14 empty] | EquivalentContinuousPriorLoad | 45.0485
[14 empty] | EquivalentContinuousPriorLoadIntervalCount | 12
[14 empty] | EquivalentContinuousPostLoad | 50.8988
[14 empty] | EquivalentContinuousPostLoadIntervalCount | 12
[14 empty] | EquivalentContinuousMaxLoad | 203.5953
[14 empty] | AmbientTemperatureF | 48.9
[14 empty] | AmbientTemperatureC | 9.3889
[14 empty] | TemperatureBelowThirtyMultiplier | 20.6111
[14 empty] | TemperatureAboveThirtyMultiplier | 0
TransformerID | TransformerIDentifier | TransformerName | LocationNumber | SubstationName | FeederName | ReadDate | kVAReadValue | kWValue | KVARating | kVaSqaured | OverRating | ReadLogDate | PercentLoad | DateMaxLoadDuration | 2018-03-08 03:00
94 | OH63572927003 | OH63572927003 | 102205203 | Sub 1 | 5 | 2018-03-06 18:00 | 45.12 | 40.608 | 25 | 2035.8144 | 1 | 43165 | 1.8048 | DateMinLoadDuration | 2018-03-07 06:00
94 | OH63572927003 | OH63572927003 | 102205203 | Sub 1 | 5 | 2018-03-06 19:00 | 47.76 | 42.984 | 25 | 2281.0176 | 1 | 43165 | 1.9104 | LoadDurationHours | 22
94 | OH63572927003 | OH63572927003 | 102205203 | Sub 1 | 5 | 2018-03-06 20:00 | 50.36 | 45.324 | 25 | 2536.1296 | 1 | 43165 | 2.0144 | AllowableLoadingPercentageColumn | Ninety
94 | OH63572927003 | OH63572927003 | 102205203 | Sub 1 | 5 | 2018-03-06 21:00 | 48.88 | 43.992 | 25 | 2389.2544 | 1 | 43165 | 1.9552 | AllowableLoadingPercentage | 130.6111
94 | OH63572927003 | OH63572927003 | 102205203 | Sub 1 | 5 | 2018-03-06 22:00 | 48.48 | 43.632 | 25 | 2350.3104 | 1 | 43165 | 1.9392 | ActualLoadingPercentage | 249.64 | transformer is over loaded
94 | OH63572927003 | OH63572927003 | 102205203 | Sub 1 | 5 | 2018-03-06 23:00 | 52.76 | 47.484 | 25 | 2783.6176 | 1 | 43165 | 2.1104 | TransformerRatingPredictedChoice | 50
94 | OH63572927003 | OH63572927003 | 102205203 | Sub 1 | 5 | 2018-03-07 | 55.36 | 49.824 | 25 | 3064.7296 | 1 | 43165 | 2.2144 | TransformerRatingPredictedLoadingPercentage | 124.82
94 | OH63572927003 | OH63572927003 | 102205203 | Sub 1 | 5 | 2018-03-07 01:00 | 55.08 | 49.572 | 25 | 3033.8064 | 1 | 43166 | 2.2032 | CreatedDate | 43168.6234
94 | OH63572927003 | OH63572927003 | 102205203 | Sub 1 | 5 | 2018-03-07 02:00 | 53.08 | 47.772 | 25 | 2817.4864 | 1 | 43166 | 2.1232
94 | OH63572927003 | OH63572927003 | 102205203 | Sub 1 | 5 | 2018-03-07 03:00 | 30.36 | 27.324 | 25 | 921.7296 | 1 | 43166 | 1.2144 | DurationHrs | Fifty | SeventyFive | Ninety
94 | OH63572927003 | OH63572927003 | 102205203 | Sub 1 | 5 | 2018-03-07 04:00 | 8.12 | 7.308 | 25 | 65.9344 | 0 | 43166 | 0.3248 | 1 | 232.6111 | 216.6111 | 202.6111
94 | OH63572927003 | OH63572927003 | 102205203 | Sub 1 | 5 | 2018-03-07 05:00 | 8.52 | 7.668 | 25 | 72.5904 | 0 | 43166 | 0.3408 | 2 | 199.6111 | 188.6111 | 177.6111
94 | OH63572927003 | OH63572927003 | 102205203 | Sub 1 | 5 | 2018-03-07 06:00 | 32.52 | 29.268 | 25 | 1057.5504 | 1 | 43166 | 1.3008 | 4 | 170.6111 | 164.6111 | 156.6111
94 | OH63572927003 | OH63572927003 | 102205203 | Sub 1 | 5 | 2018-03-07 07:00 | 53.64 | 48.276 | 25 | 2877.2496 | 1 | 43166 | 2.1456 | 6 | 154.6111 | 151.6111 | 146.6111
94 | OH63572927003 | OH63572927003 | 102205203 | Sub 1 | 5 | 2018-03-07 08:00 | 55.68 | 50.112 | 25 | 3100.2624 | 1 | 43166 | 2.2272 | 8 | 148.6111 | 145.6111 | 141.6111
94 | OH63572927003 | OH63572927003 | 102205203 | Sub 1 | 5 | 2018-03-07 09:00 | 56.16 | 50.544 | 25 | 3153.9456 | 1 | 43166 | 2.2464 | 12 | 142.6111 | 139.6111 | 137.6111
94 | OH63572927003 | OH63572927003 | 102205203 | Sub 1 | 5 | 2018-03-07 10:00 | 57.2 | 51.48 | 25 | 3271.84 | 1 | 43166 | 2.288 | 16 | 137.6111 | 135.6111 | 133.6111
94 | OH63572927003 | OH63572927003 | 102205203 | Sub 1 | 5 | 2018-03-07 11:00 | 57.92 | 52.128 | 25 | 3354.7264 | 1 | 43166 | 2.3168 | 20 | 133.6111 | 131.6111 | 130.6111
94 | OH63572927003 | OH63572927003 | 102205203 | Sub 1 | 5 | 2018-03-07 12:00 | 58.16 | 52.344 | 25 | 3382.5856 | 1 | 43166 | 2.3264 | 24 | 128.6111 | 127.6111 | 127.6111
94 | OH63572927003 | OH63572927003 | 102205203 | Sub 1 | 5 | 2018-03-07 13:00 | 54.72 | 49.248 | 25 | 2994.2784 | 1 | 43166 | 2.1888
94 | OH63572927003 | OH63572927003 | 102205203 | Sub 1 | 5 | 2018-03-07 14:00 | 59.229 | 53.306 | 25 | 3508.0744 | 1 | 43166 | 2.3692
94 | OH63572927003 | OH63572927003 | 102205203 | Sub 1 | 5 | 2018-03-07 15:00 | 57.128 | 51.415 | 25 | 3263.6084 | 1 | 43166 | 2.2851
94 | OH63572927003 | OH63572927003 | 102205203 | Sub 1 | 5 | 2018-03-07 16:00 | 62.41 | 56.169 | 25 | 3895.0081 | 1 | 43166 | 2.4964
94 | OH63572927003 | OH63572927003 | 102205203 | Sub 1 | 5 | 2018-03-07 17:00 | 47.28 | 42.552 | 25 | 2235.3984 | 1 | 43166 | 1.8912
94 | OH63572927003 | OH63572927003 | 102205203 | Sub 1 | 5 | 2018-03-07 18:00 | 47.36 | 42.624 | 25 | 2242.9696 | 1 | 43166 | 1.8944
94 | OH63572927003 | OH63572927003 | 102205203 | Sub 1 | 5 | 2018-03-07 19:00 | 49.76 | 44.784 | 25 | 2476.0576 | 1 | 43166 | 1.9904
94 | OH63572927003 | OH63572927003 | 102205203 | Sub 1 | 5 | 2018-03-07 20:00 | 51.04 | 45.936 | 25 | 2605.0816 | 1 | 43166 | 2.0416
94 | OH63572927003 | OH63572927003 | 102205203 | Sub 1 | 5 | 2018-03-07 21:00 | 56.08 | 50.472 | 25 | 3144.9664 | 1 | 43166 | 2.2432
94 | OH63572927003 | OH63572927003 | 102205203 | Sub 1 | 5 | 2018-03-07 22:00 | 55.48 | 49.932 | 25 | 3078.0304 | 1 | 43166 | 2.2192
94 | OH63572927003 | OH63572927003 | 102205203 | Sub 1 | 5 | 2018-03-07 23:00 | 54.04 | 48.636 | 25 | 2920.3216 | 1 | 43166 | 2.1616
94 | OH63572927003 | OH63572927003 | 102205203 | Sub 1 | 5 | 2018-03-08 | 54.28 | 48.852 | 25 | 2946.3184 | 1 | 43166 | 2.1712
94 | OH63572927003 | OH63572927003 | 102205203 | Sub 1 | 5 | 2018-03-08 01:00 | 55.28 | 49.752 | 25 | 3055.8784 | 1 | 43167 | 2.2112
94 | OH63572927003 | OH63572927003 | 102205203 | Sub 1 | 5 | 2018-03-08 02:00 | 54.68 | 49.212 | 25 | 2989.9024 | 1 | 43167 | 2.1872
94 | OH63572927003 | OH63572927003 | 102205203 | Sub 1 | 5 | 2018-03-08 03:00 | 25.24 | 22.716 | 25 | 637.0576 | 1 | 43167 | 1.0096
94 | OH63572927003 | OH63572927003 | 102205203 | Sub 1 | 5 | 2018-03-08 04:00 | 8.56 | 7.704 | 25 | 73.2736 | 0 | 43167 | 0.3424
94 | OH63572927003 | OH63572927003 | 102205203 | Sub 1 | 5 | 2018-03-08 05:00 | 8.8 | 7.92 | 25 | 77.44 | 0 | 43167 | 0.352
94 | OH63572927003 | OH63572927003 | 102205203 | Sub 1 | 5 | 2018-03-08 06:00 | 32.68 | 29.412 | 25 | 1067.9824 | 1 | 43167 | 1.3072
94 | OH63572927003 | OH63572927003 | 102205203 | Sub 1 | 5 | 2018-03-08 07:00 | 54.52 | 49.068 | 25 | 2972.4304 | 1 | 43167 | 2.1808
94 | OH63572927003 | OH63572927003 | 102205203 | Sub 1 | 5 | 2018-03-08 08:00 | 56.48 | 50.832 | 25 | 3189.9904 | 1 | 43167 | 2.2592
94 | OH63572927003 | OH63572927003 | 102205203 | Sub 1 | 5 | 2018-03-08 09:00 | 56.96 | 51.264 | 25 | 3244.4416 | 1 | 43167 | 2.2784
94 | OH63572927003 | OH63572927003 | 102205203 | Sub 1 | 5 | 2018-03-08 10:00 | 58.04 | 52.236 | 25 | 3368.6416 | 1 | 43167 | 2.3216
94 | OH63572927003 | OH63572927003 | 102205203 | Sub 1 | 5 | 2018-03-08 11:00 | 58.96 | 53.064 | 25 | 3476.2816 | 1 | 43167 | 2.3584
94 | OH63572927003 | OH63572927003 | 102205203 | Sub 1 | 5 | 2018-03-08 12:00 | 59.76 | 53.784 | 25 | 3571.2576 | 1 | 43167 | 2.3904
94 | OH63572927003 | OH63572927003 | 102205203 | Sub 1 | 5 | 2018-03-08 13:00 | 56.24 | 50.616 | 25 | 3162.9376 | 1 | 43167 | 2.2496
94 | OH63572927003 | OH63572927003 | 102205203 | Sub 1 | 5 | 2018-03-08 14:00 | 57.76 | 51.984 | 25 | 3336.2176 | 1 | 43167 | 2.3104
94 | OH63572927003 | OH63572927003 | 102205203 | Sub 1 | 5 | 2018-03-08 15:00 | 59.56 | 53.604 | 25 | 3547.3936 | 1 | 43167 | 2.3824
|  |  | TransformerID | 94
|  |  | TransformerIDentifier | OH63572927003
|  |  | TransformerName | OH63572927003
|  |  | LocationNumber | 102205203
|  |  | SubstationName | Sub 1
|  |  | FeederName | 5
|  |  | kVAmin | 6.84
|  |  | kVAmax | 62.41
|  |  | kVAavg | 29.8928
|  |  | kVAmaxDate | 43166.6667
|  |  | DateMin | 43092.0417
|  |  | DateMax | 43169
|  |  | kVARating | 25
|  |  | EquivalentContinuousPriorLoad | 45.0485
|  |  | EquivalentContinuousPriorLoadIntervalCount | 12
|  |  | EquivalentContinuousPostLoad | 50.8988
|  |  | EquivalentContinuousPostLoadIntervalCount | 12
|  |  | EquivalentContinuousMaxLoad | 203.5953
|  |  | AmbientTemperatureF | 48.9
|  |  | AmbientTemperatureC | 9.3889
|  |  | TemperatureBelowThirtyMultiplier | 20.6111
|  |  | TemperatureAboveThirtyMultiplier | 0
|  |  | DateMaxLoadDuration | 43167.125
|  |  | DateMinLoadDuration | 43166.25
|  |  | LoadDurationHours | 22
|  |  | AllowableLoadingPercentageColumn | Ninety
|  |  | AllowableLoadingPercentage | 130.6111
|  |  | ActualLoadingPercentage | 249.64
|  |  | TransformerRatingPredictedChoice | NULL
|  |  | TransformerRatingPredictedLoadingPercentage | NULL
|  |  | CreatedDate | 43168.6234

## 2 Durations-OH64564397005
Transformer is overloaded by contains one value in load duration which is included in the load duration, but below the kVARating. Intersting….
[14 empty] | TransformerID | 232
[14 empty] | TransformerIDentifier | OH64564397005
[14 empty] | TransformerName | OH64564397005
[14 empty] | LocationNumber | 102101978
[14 empty] | SubstationName | Sub 2
[14 empty] | FeederName | 4
[14 empty] | kVAmin | 0.144
[14 empty] | kVAmax | 1.593
[14 empty] | kVAavg | 0.57786
[14 empty] | kVAmaxDate | 43168.75
[14 empty] | DateMin | 43092.0417
[14 empty] | DateMax | 43172
[14 empty] | kVARating | 1
[14 empty] | EquivalentContinuousPriorLoad | 0.27432
[14 empty] | EquivalentContinuousPriorLoadIntervalCount | 12
[14 empty] | EquivalentContinuousPostLoad | 0.73504
[14 empty] | EquivalentContinuousPostLoadIntervalCount | 12
[14 empty] | EquivalentContinuousMaxLoad | 73.5041
[14 empty] | AmbientTemperatureF | 36
[14 empty] | AmbientTemperatureC | 2.2222
[14 empty] | TemperatureBelowThirtyMultiplier | 27.7778
[14 empty] | TemperatureAboveThirtyMultiplier | 0
[14 empty] | DateMaxLoadDuration | 2018-03-09 19:00
TransformerID | TransformerIDentifier | TransformerName | LocationNumber | SubstationName | FeederName | ReadDate | kVAReadValue | kWValue | KVARating | kVaSqaured | OverRating | ReadLogDate | PercentLoad | DateMinLoadDuration | 2018-03-09 12:00
232 | OH64564397005 | OH64564397005 | 102101978 | Sub 2 | 4 | 2018-03-09 | 0.253 | 0.228 | 1 | 0.064009 | 0 | 43167 | 0.253 | LoadDurationHours | 7
232 | OH64564397005 | OH64564397005 | 102101978 | Sub 2 | 4 | 2018-03-09 01:00 | 0.255 | 0.23 | 1 | 0.065025 | 0 | 43168 | 0.255 | AllowableLoadingPercentageColumn | SeventyFive
232 | OH64564397005 | OH64564397005 | 102101978 | Sub 2 | 4 | 2018-03-09 02:00 | 0.251 | 0.226 | 1 | 0.063001 | 0 | 43168 | 0.251 | AllowableLoadingPercentage | 158.7778
232 | OH64564397005 | OH64564397005 | 102101978 | Sub 2 | 4 | 2018-03-09 03:00 | 0.253 | 0.228 | 1 | 0.064009 | 0 | 43168 | 0.253 | ActualLoadingPercentage | 159.3 | transformer is over loaded
232 | OH64564397005 | OH64564397005 | 102101978 | Sub 2 | 4 | 2018-03-09 04:00 | 0.253 | 0.228 | 1 | 0.064009 | 0 | 43168 | 0.253 | TransformerRatingPredictedChoice | 10
232 | OH64564397005 | OH64564397005 | 102101978 | Sub 2 | 4 | 2018-03-09 05:00 | 0.251 | 0.226 | 1 | 0.063001 | 0 | 43168 | 0.251 | TransformerRatingPredictedLoadingPercentage | 15.93
232 | OH64564397005 | OH64564397005 | 102101978 | Sub 2 | 4 | 2018-03-09 06:00 | 0.253 | 0.228 | 1 | 0.064009 | 0 | 43168 | 0.253 | CreatedDate | 43171.4141
232 | OH64564397005 | OH64564397005 | 102101978 | Sub 2 | 4 | 2018-03-09 07:00 | 0.255 | 0.23 | 1 | 0.065025 | 0 | 43168 | 0.255
232 | OH64564397005 | OH64564397005 | 102101978 | Sub 2 | 4 | 2018-03-09 08:00 | 0.255 | 0.23 | 1 | 0.065025 | 0 | 43168 | 0.255
232 | OH64564397005 | OH64564397005 | 102101978 | Sub 2 | 4 | 2018-03-09 09:00 | 0.251 | 0.226 | 1 | 0.063001 | 0 | 43168 | 0.251 | DurationHrs | Fifty | SeventyFive | Ninety
232 | OH64564397005 | OH64564397005 | 102101978 | Sub 2 | 4 | 2018-03-09 10:00 | 0.253 | 0.228 | 1 | 0.064009 | 0 | 43168 | 0.253 | 1 | 239.7778 | 223.7778 | 209.7778
232 | OH64564397005 | OH64564397005 | 102101978 | Sub 2 | 4 | 2018-03-09 11:00 | 0.446 | 0.402 | 1 | 0.19892 | 0 | 43168 | 0.446 | 2 | 206.7778 | 195.7778 | 184.7778
232 | OH64564397005 | OH64564397005 | 102101978 | Sub 2 | 4 | 2018-03-09 12:00 | 1.477 | 1.33 | 1 | 2.1815 | 1 | 43168 | 1.477 | 4 | 177.7778 | 171.7778 | 163.7778
232 | OH64564397005 | OH64564397005 | 102101978 | Sub 2 | 4 | 2018-03-09 13:00 | 1.257 | 1.132 | 1 | 1.58 | 1 | 43168 | 1.257 | 6 | 161.7778 | 158.7778 | 153.7778
232 | OH64564397005 | OH64564397005 | 102101978 | Sub 2 | 4 | 2018-03-09 14:00 | 1.173 | 1.056 | 1 | 1.3759 | 1 | 43168 | 1.173 | 8 | 155.7778 | 152.7778 | 148.7778
232 | OH64564397005 | OH64564397005 | 102101978 | Sub 2 | 4 | 2018-03-09 15:00 | 1.22 | 1.098 | 1 | 1.4884 | 1 | 43168 | 1.22 | 12 | 149.7778 | 146.7778 | 144.7778
232 | OH64564397005 | OH64564397005 | 102101978 | Sub 2 | 4 | 2018-03-09 16:00 | 1.222 | 1.1 | 1 | 1.4933 | 1 | 43168 | 1.222 | 16 | 144.7778 | 142.7778 | 140.7778
232 | OH64564397005 | OH64564397005 | 102101978 | Sub 2 | 4 | 2018-03-09 17:00 | 0.968 | 0.872 | 1 | 0.93702 | 0 | 43168 | 0.968 | 20 | 140.7778 | 138.7778 | 137.7778
232 | OH64564397005 | OH64564397005 | 102101978 | Sub 2 | 4 | 2018-03-09 18:00 | 1.593 | 1.434 | 1 | 2.5376 | 1 | 43168 | 1.593 | 24 | 135.7778 | 134.7778 | 134.7778
232 | OH64564397005 | OH64564397005 | 102101978 | Sub 2 | 4 | 2018-03-09 19:00 | 1.24 | 1.116 | 1 | 1.5376 | 1 | 43168 | 1.24
232 | OH64564397005 | OH64564397005 | 102101978 | Sub 2 | 4 | 2018-03-09 20:00 | 0.724 | 0.652 | 1 | 0.52418 | 0 | 43168 | 0.724
232 | OH64564397005 | OH64564397005 | 102101978 | Sub 2 | 4 | 2018-03-09 21:00 | 0.74 | 0.666 | 1 | 0.5476 | 0 | 43168 | 0.74
232 | OH64564397005 | OH64564397005 | 102101978 | Sub 2 | 4 | 2018-03-09 22:00 | 0.746 | 0.672 | 1 | 0.55652 | 0 | 43168 | 0.746
232 | OH64564397005 | OH64564397005 | 102101978 | Sub 2 | 4 | 2018-03-09 23:00 | 0.737 | 0.664 | 1 | 0.54317 | 0 | 43168 | 0.737
232 | OH64564397005 | OH64564397005 | 102101978 | Sub 2 | 4 | 2018-03-10 | 0.742 | 0.668 | 1 | 0.55056 | 0 | 43168 | 0.742
232 | OH64564397005 | OH64564397005 | 102101978 | Sub 2 | 4 | 2018-03-10 01:00 | 0.74 | 0.666 | 1 | 0.5476 | 0 | 43169 | 0.74
232 | OH64564397005 | OH64564397005 | 102101978 | Sub 2 | 4 | 2018-03-10 02:00 | 0.748 | 0.674 | 1 | 0.5595 | 0 | 43169 | 0.748
232 | OH64564397005 | OH64564397005 | 102101978 | Sub 2 | 4 | 2018-03-10 03:00 | 0.742 | 0.668 | 1 | 0.55056 | 0 | 43169 | 0.742
232 | OH64564397005 | OH64564397005 | 102101978 | Sub 2 | 4 | 2018-03-10 04:00 | 0.74 | 0.666 | 1 | 0.5476 | 0 | 43169 | 0.74
232 | OH64564397005 | OH64564397005 | 102101978 | Sub 2 | 4 | 2018-03-10 05:00 | 0.742 | 0.668 | 1 | 0.55056 | 0 | 43169 | 0.742
232 | OH64564397005 | OH64564397005 | 102101978 | Sub 2 | 4 | 2018-03-10 06:00 | 0.68 | 0.612 | 1 | 0.4624 | 0 | 43169 | 0.68
232 | OH64564397005 | OH64564397005 | 102101978 | Sub 2 | 4 | 2018-03-10 07:00 | 0.737 | 0.664 | 1 | 0.54317 | 0 | 43169 | 0.737
[5 empty] | DurationHrs | Fifty | SeventyFive | Ninety | DiffToNextValue
[5 empty] | 1 | 239.7778 | 223.7778 | 209.7778 | 1
[5 empty] | 2 | 206.7778 | 195.7778 | 184.7778 | 2
[5 empty] | 4 | 177.7778 | 171.7778 | 163.7778 | 2
[5 empty] | 6 | 161.7778 | 158.7778 | 153.7778 | 2
[5 empty] | 8 | 155.7778 | 152.7778 | 148.7778 | 4
[5 empty] | 12 | 149.7778 | 146.7778 | 144.7778 | 4
[5 empty] | 16 | 144.7778 | 142.7778 | 140.7778 | 4
[5 empty] | 20 | 140.7778 | 138.7778 | 137.7778 | 4
[5 empty] | 24 | 135.7778 | 134.7778 | 134.7778 | 4

## 1 Duration-OH64566256012
[14 empty] | TransformerID | 266
[14 empty] | TransformerIDentifier | OH64566256012
[14 empty] | TransformerName | OH64566256012
[14 empty] | LocationNumber | 401112758
[14 empty] | SubstationName | Sub 2
[14 empty] | FeederName | 4
[14 empty] | kVAmin | 0.926
[14 empty] | kVAmax | 10.182
[14 empty] | kVAavg | 2.6271
[14 empty] | kVAmaxDate | 43131.7917
[14 empty] | DateMin | 43092.0417
[14 empty] | DateMax | 43172
[14 empty] | kVARating | 10
[14 empty] | EquivalentContinuousPriorLoad | 3.4942
[14 empty] | EquivalentContinuousPriorLoadIntervalCount | 12
[14 empty] | EquivalentContinuousPostLoad | 2.6425
[14 empty] | EquivalentContinuousPostLoadIntervalCount | 12
[14 empty] | EquivalentContinuousMaxLoad | 34.9425
[14 empty] | AmbientTemperatureF | 28.3
TransformerID | TransformerIDentifier | TransformerName | LocationNumber | SubstationName | FeederName | ReadDate | kVAReadValue | kWValue | KVARating | kVaSqaured | OverRating | ReadLogDate | PercentLoad | AmbientTemperatureC | -2.0556
266 | OH64566256012 | OH64566256012 | 401112758 | Sub 2 | 4 | 43131.2917 | 1.871 | 1.684 | 10 | 3.5006 | 0 | 43131 | 0.1871 | TemperatureBelowThirtyMultiplier | 32.0556
266 | OH64566256012 | OH64566256012 | 401112758 | Sub 2 | 4 | 43131.3333 | 4.877 | 4.39 | 10 | 23.7851 | 0 | 43131 | 0.4877 | TemperatureAboveThirtyMultiplier | 0
266 | OH64566256012 | OH64566256012 | 401112758 | Sub 2 | 4 | 43131.375 | 5.235 | 4.712 | 10 | 27.4052 | 0 | 43131 | 0.5235 | DateMaxLoadDuration | 43131.7917
266 | OH64566256012 | OH64566256012 | 401112758 | Sub 2 | 4 | 43131.4167 | 1.726 | 1.554 | 10 | 2.9791 | 0 | 43131 | 0.1726 | DateMinLoadDuration | 43131.7917
266 | OH64566256012 | OH64566256012 | 401112758 | Sub 2 | 4 | 43131.4583 | 1.186 | 1.068 | 10 | 1.4066 | 0 | 43131 | 0.1186 | LoadDurationHours | 1
266 | OH64566256012 | OH64566256012 | 401112758 | Sub 2 | 4 | 43131.5 | 1.12 | 1.008 | 10 | 1.2544 | 0 | 43131 | 0.112 | AllowableLoadingPercentageColumn | Fifty
266 | OH64566256012 | OH64566256012 | 401112758 | Sub 2 | 4 | 43131.5417 | 1.255 | 1.13 | 10 | 1.575 | 0 | 43131 | 0.1255 | AllowableLoadingPercentage | 244.0556
266 | OH64566256012 | OH64566256012 | 401112758 | Sub 2 | 4 | 43131.5833 | 1.771 | 1.594 | 10 | 3.1364 | 0 | 43131 | 0.1771 | ActualLoadingPercentage | 101.82 | Transformer is good to go… we are not over loaded.
266 | OH64566256012 | OH64566256012 | 401112758 | Sub 2 | 4 | 43131.625 | 5.302 | 4.772 | 10 | 28.1112 | 0 | 43131 | 0.5302 | TransformerRatingUpSized | 10
266 | OH64566256012 | OH64566256012 | 401112758 | Sub 2 | 4 | 43131.6667 | 3.746 | 3.372 | 10 | 14.0325 | 0 | 43131 | 0.3746 | TransformerRatingPredictedLoadingPercentage | 103.86
266 | OH64566256012 | OH64566256012 | 401112758 | Sub 2 | 4 | 43131.7083 | 1.688 | 1.52 | 10 | 2.8493 | 0 | 43131 | 0.1688 | CreateDate | 43171.501
266 | OH64566256012 | OH64566256012 | 401112758 | Sub 2 | 4 | 43131.75 | 6.04 | 5.436 | 10 | 36.4816 | 0 | 43131 | 0.604
266 | OH64566256012 | OH64566256012 | 401112758 | Sub 2 | 4 | 43131.7917 | 10.182 | 9.164 | 10 | 103.6731 | 1 | 43131 | 1.0182 | DurationHrs | Fifty | SeventyFive | Ninety
266 | OH64566256012 | OH64566256012 | 401112758 | Sub 2 | 4 | 43131.8333 | 4.735 | 4.262 | 10 | 22.4202 | 0 | 43131 | 0.4735 | 1 | 244.0556 | 228.0556 | 214.0556
266 | OH64566256012 | OH64566256012 | 401112758 | Sub 2 | 4 | 43131.875 | 5.486 | 4.938 | 10 | 30.0962 | 0 | 43131 | 0.5486 | 2 | 211.0556 | 200.0556 | 189.0556
266 | OH64566256012 | OH64566256012 | 401112758 | Sub 2 | 4 | 43131.9167 | 2.102 | 1.892 | 10 | 4.4184 | 0 | 43131 | 0.2102 | 4 | 182.0556 | 176.0556 | 168.0556
266 | OH64566256012 | OH64566256012 | 401112758 | Sub 2 | 4 | 43131.9583 | 2.075 | 1.868 | 10 | 4.3056 | 0 | 43131 | 0.2075 | 6 | 166.0556 | 163.0556 | 158.0556
266 | OH64566256012 | OH64566256012 | 401112758 | Sub 2 | 4 | 43132 | 1.713 | 1.542 | 10 | 2.9344 | 0 | 43131 | 0.1713 | 8 | 160.0556 | 157.0556 | 153.0556
266 | OH64566256012 | OH64566256012 | 401112758 | Sub 2 | 4 | 43132.0417 | 2.073 | 1.866 | 10 | 4.2973 | 0 | 43132 | 0.2073 | 12 | 154.0556 | 151.0556 | 149.0556
266 | OH64566256012 | OH64566256012 | 401112758 | Sub 2 | 4 | 43132.0833 | 1.468 | 1.322 | 10 | 2.155 | 0 | 43132 | 0.1468 | 16 | 149.0556 | 147.0556 | 145.0556
266 | OH64566256012 | OH64566256012 | 401112758 | Sub 2 | 4 | 43132.125 | 1.415 | 1.274 | 10 | 2.0022 | 0 | 43132 | 0.1415 | 20 | 145.0556 | 143.0556 | 142.0556
266 | OH64566256012 | OH64566256012 | 401112758 | Sub 2 | 4 | 43132.1667 | 1.453 | 1.308 | 10 | 2.1112 | 0 | 43132 | 0.1453 | 24 | 140.0556 | 139.0556 | 139.0556
266 | OH64566256012 | OH64566256012 | 401112758 | Sub 2 | 4 | 43132.2083 | 1.406 | 1.266 | 10 | 1.9768 | 0 | 43132 | 0.1406
266 | OH64566256012 | OH64566256012 | 401112758 | Sub 2 | 4 | 43132.25 | 1.88 | 1.692 | 10 | 3.5344 | 0 | 43132 | 0.188
266 | OH64566256012 | OH64566256012 | 401112758 | Sub 2 | 4 | 43132.2917 | 1.882 | 1.694 | 10 | 3.5419 | 0 | 43132 | 0.1882

## Oversize-Tx OH65572927002
[14 empty] | TransformerID | 374
[14 empty] | TransformerIDentifier | OH65572927002
[14 empty] | TransformerName | OH65572927002
[14 empty] | LocationNumber | 101400032
[14 empty] | SubstationName | Sub 1
[14 empty] | FeederName | 2
[14 empty] | kVAmin | 0.008
[14 empty] | kVAmax | 0.077
[14 empty] | kVAavg | 0.011219
[14 empty] | kVAmaxDate | 43133.3333
[14 empty] | DateMin | 43092.0417
[14 empty] | DateMax | 43172
[14 empty] | kVARating | 1
[14 empty] | EquivalentContinuousPriorLoad | 0.008544
[14 empty] | EquivalentContinuousPriorLoadIntervalCount | 12
[14 empty] | EquivalentContinuousPostLoad | 0.012443
[14 empty] | EquivalentContinuousPostLoadIntervalCount | 12
[14 empty] | EquivalentContinuousMaxLoad | 1.2443
[14 empty] | AmbientTemperatureF | 15.1
[14 empty] | AmbientTemperatureC | -9.3889
[14 empty] | TemperatureBelowThirtyMultiplier | 39.3889
TransformerID | TransformerIDentifier | TransformerName | LocationNumber | SubstationName | FeederName | ReadDate | kVAReadValue | kWValue | KVARating | kVaSqaured | OverRating | ReadLogDate | PercentLoad | TemperatureAboveThirtyMultiplier | 0
374 | OH65572927002 | OH65572927002 | 101400032 | Sub 1 | 2 | 43132.7917 | 0.008 | 0.007 | 1 | 6.4e-05 | 0 | 43132 | 0.008 | DateMaxLoadDuration | 43133.375
374 | OH65572927002 | OH65572927002 | 101400032 | Sub 1 | 2 | 43132.8333 | 0.008 | 0.007 | 1 | 6.4e-05 | 0 | 43132 | 0.008 | DateMinLoadDuration | 43133.2917
374 | OH65572927002 | OH65572927002 | 101400032 | Sub 1 | 2 | 43132.875 | 0.01 | 0.009 | 1 | 0.0001 | 0 | 43132 | 0.01 | LoadDurationHours | 3
374 | OH65572927002 | OH65572927002 | 101400032 | Sub 1 | 2 | 43132.9167 | 0.008 | 0.007 | 1 | 6.4e-05 | 0 | 43132 | 0.008 | AllowableLoadingPercentageColumn | Fifty
374 | OH65572927002 | OH65572927002 | 101400032 | Sub 1 | 2 | 43132.9583 | 0.01 | 0.009 | 1 | 0.0001 | 0 | 43132 | 0.01 | AllowableLoadingPercentage | 218.3889
374 | OH65572927002 | OH65572927002 | 101400032 | Sub 1 | 2 | 43133 | 0.008 | 0.007 | 1 | 6.4e-05 | 0 | 43132 | 0.008 | ActualLoadingPercentage | 7.7
374 | OH65572927002 | OH65572927002 | 101400032 | Sub 1 | 2 | 43133.0417 | 0.008 | 0.007 | 1 | 6.4e-05 | 0 | 43133 | 0.008 | TransformerRatingUpSized | 1
374 | OH65572927002 | OH65572927002 | 101400032 | Sub 1 | 2 | 43133.0833 | 0.008 | 0.007 | 1 | 6.4e-05 | 0 | 43133 | 0.008 | TransformerRatingPredictedLoadingPercentage | 7.7
374 | OH65572927002 | OH65572927002 | 101400032 | Sub 1 | 2 | 43133.125 | 0.01 | 0.009 | 1 | 0.0001 | 0 | 43133 | 0.01 | CreateDate | 24:00
374 | OH65572927002 | OH65572927002 | 101400032 | Sub 1 | 2 | 43133.1667 | 0.008 | 0.007 | 1 | 6.4e-05 | 0 | 43133 | 0.008
374 | OH65572927002 | OH65572927002 | 101400032 | Sub 1 | 2 | 43133.2083 | 0.008 | 0.007 | 1 | 6.4e-05 | 0 | 43133 | 0.008
374 | OH65572927002 | OH65572927002 | 101400032 | Sub 1 | 2 | 43133.25 | 0.008 | 0.007 | 1 | 6.4e-05 | 0 | 43133 | 0.008 | DurationHrs | Fifty | SeventyFive | Ninety | DiffToNextValue
374 | OH65572927002 | OH65572927002 | 101400032 | Sub 1 | 2 | 43133.2917 | 0.01 | 0.009 | 1 | 0.0001 | 0 | 43133 | 0.01 | 1 | 251.3889 | 235.3889 | 221.3889 | 1
374 | OH65572927002 | OH65572927002 | 101400032 | Sub 1 | 2 | 43133.3333 | 0.077 | 0.069 | 1 | 0.005929 | 0 | 43133 | 0.077 | 2 | 218.3889 | 207.3889 | 196.3889 | 2
374 | OH65572927002 | OH65572927002 | 101400032 | Sub 1 | 2 | 43133.375 | 0.008 | 0.007 | 1 | 6.4e-05 | 0 | 43133 | 0.008 | 4 | 189.3889 | 183.3889 | 175.3889 | 2
374 | OH65572927002 | OH65572927002 | 101400032 | Sub 1 | 2 | 43133.4167 | 0.01 | 0.009 | 1 | 0.0001 | 0 | 43133 | 0.01 | 6 | 173.3889 | 170.3889 | 165.3889 | 2
374 | OH65572927002 | OH65572927002 | 101400032 | Sub 1 | 2 | 43133.4583 | 0.008 | 0.007 | 1 | 6.4e-05 | 0 | 43133 | 0.008 | 8 | 167.3889 | 164.3889 | 160.3889 | 4
374 | OH65572927002 | OH65572927002 | 101400032 | Sub 1 | 2 | 43133.5 | 0.021 | 0.019 | 1 | 0.000441 | 0 | 43133 | 0.021 | 12 | 161.3889 | 158.3889 | 156.3889 | 4
374 | OH65572927002 | OH65572927002 | 101400032 | Sub 1 | 2 | 43133.5417 | 0.01 | 0.009 | 1 | 0.0001 | 0 | 43133 | 0.01 | 16 | 156.3889 | 154.3889 | 152.3889 | 4
374 | OH65572927002 | OH65572927002 | 101400032 | Sub 1 | 2 | 43133.5833 | 0.008 | 0.007 | 1 | 6.4e-05 | 0 | 43133 | 0.008 | 20 | 152.3889 | 150.3889 | 149.3889 | 4
374 | OH65572927002 | OH65572927002 | 101400032 | Sub 1 | 2 | 43133.625 | 0.01 | 0.009 | 1 | 0.0001 | 0 | 43133 | 0.01 | 24 | 147.3889 | 146.3889 | 146.3889 | 4
374 | OH65572927002 | OH65572927002 | 101400032 | Sub 1 | 2 | 43133.6667 | 0.01 | 0.009 | 1 | 0.0001 | 0 | 43133 | 0.01
374 | OH65572927002 | OH65572927002 | 101400032 | Sub 1 | 2 | 43133.7083 | 0.008 | 0.007 | 1 | 6.4e-05 | 0 | 43133 | 0.008
374 | OH65572927002 | OH65572927002 | 101400032 | Sub 1 | 2 | 43133.75 | 0.008 | 0.007 | 1 | 6.4e-05 | 0 | 43133 | 0.008
374 | OH65572927002 | OH65572927002 | 101400032 | Sub 1 | 2 | 43133.7917 | 0.016 | 0.014 | 1 | 0.000256 | 0 | 43133 | 0.016
374 | OH65572927002 | OH65572927002 | 101400032 | Sub 1 | 2 | 43133.8333 | 0.008 | 0.007 | 1 | 6.4e-05 | 0 | 43133 | 0.008
374 | OH65572927002 | OH65572927002 | 101400032 | Sub 1 | 2 | 43133.875 | 0.021 | 0.019 | 1 | 0.000441 | 0 | 43133 | 0.021

## OH65566592004-A
| ReadDate | kVAReadValue | kWValue | KVARating | kVaSqaured | ActualLoadPercentage | OverRating
1 | 2018-02-12 19:00 | 110.666 | 99.6 | 225 | 12246.9636 | 202.1911 | 0
2 | 2018-02-12 20:00 | 97.066 | 87.36 | 225 | 9421.8084 | 202.1911 | 0
3 | 2018-02-12 21:00 | 104 | 93.6 | 225 | 10816 | 202.1911 | 0
4 | 2018-02-12 22:00 | 104.8 | 94.32 | 225 | 10983.04 | 202.1911 | 0
5 | 2018-02-12 23:00 | 132.533 | 119.28 | 225 | 17564.9961 | 202.1911 | 0
6 | 2018-02-13 | 110.133 | 99.12 | 225 | 12129.2777 | 202.1911 | 0
7 | 2018-02-13 01:00 | 112.266 | 101.04 | 225 | 12603.6548 | 202.1911 | 0
8 | 2018-02-13 02:00 | 108.266 | 97.44 | 225 | 11721.5268 | 202.1911 | 0
9 | 2018-02-13 03:00 | 128.8 | 115.92 | 225 | 16589.44 | 202.1911 | 0
10 | 2018-02-13 04:00 | 119.2 | 107.28 | 225 | 14208.64 | 202.1911 | 0
11 | 2018-02-13 05:00 | 134.133 | 120.72 | 225 | 17991.6617 | 202.1911 | 0
12 | 2018-02-13 06:00 | 165.6 | 149.04 | 225 | 27423.36 | 202.1911 | 0
| 2018-02-13 07:00 | 454.933 | 409.44 | 225 | 206964.0345 | 202.1911 | 1 | 1
| 2018-02-13 08:00 | 453.333 | 408 | 225 | 205510.8089 | 202.1911 | 1 | 2
| 2018-02-13 09:00 | 439.2 | 395.28 | 225 | 192896.64 | 202.1911 | 1 | 3
| 2018-02-13 10:00 | 326.933 | 294.24 | 225 | 106885.1865 | 202.1911 | 1 | 4
| 2018-02-13 11:00 | 285.866 | 257.28 | 225 | 81719.37 | 202.1911 | 1 | 5
| 2018-02-13 12:00 | 290.133 | 261.12 | 225 | 84177.1577 | 202.1911 | 1 | 6
| 2018-02-13 13:00 | 288.266 | 259.44 | 225 | 83097.2868 | 202.1911 | 1 | 7
| 2018-02-13 14:00 | 292.8 | 263.52 | 225 | 85731.84 | 202.1911 | 1 | 8
| 2018-02-13 15:00 | 289.866 | 260.88 | 225 | 84022.298 | 202.1911 | 1 | 9
| 2018-02-13 16:00 | 268 | 241.2 | 225 | 71824 | 202.1911 | 1 | 10
| 2018-02-13 17:00 | 268.266 | 241.44 | 225 | 71966.6468 | 202.1911 | 1 | 11
1 | 2018-02-13 18:00 | 152.8 | 137.52 | 225 | 23347.84 | 202.1911 | 0
2 | 2018-02-13 19:00 | 166.666 | 150 | 225 | 27777.5556 | 202.1911 | 0
3 | 2018-02-13 20:00 | 165.6 | 149.04 | 225 | 27423.36 | 202.1911 | 0
4 | 2018-02-13 21:00 | 118.933 | 107.04 | 225 | 14145.0585 | 202.1911 | 0
5 | 2018-02-13 22:00 | 105.066 | 94.56 | 225 | 11038.8644 | 202.1911 | 0
6 | 2018-02-13 23:00 | 112.8 | 101.52 | 225 | 12723.84 | 202.1911 | 0
7 | 2018-02-14 | 97.066 | 87.36 | 225 | 9421.8084 | 202.1911 | 0
8 | 2018-02-14 01:00 | 103.733 | 93.36 | 225 | 10760.5353 | 202.1911 | 0
9 | 2018-02-14 02:00 | 102.133 | 91.92 | 225 | 10431.1497 | 202.1911 | 0
10 | 2018-02-14 03:00 | 101.333 | 91.2 | 225 | 10268.3769 | 202.1911 | 0
11 | 2018-02-14 04:00 | 99.2 | 89.28 | 225 | 9840.64 | 202.1911 | 0
12 | 2018-02-14 05:00 | 122.666 | 110.4 | 225 | 15046.9476 | 202.1911 | 0
173700.3689
11 Hours Above the kVa Rating so this equates to 12 hours
Actual Loading Percentage |  |  | 202.1924
Equivalent Pre Loading Calculation |  |  | 120.3122
Equivalent Post Loading Calculation |  |  | 123.2295
Pre Loading Condition Test Value |  |  | 54.7686 | Yeilds | 75 Percent
Ambient TempF |  | 86 |  | No Temperature Data Available set to 86 as default
Ambient TempC |  | 30
Allowable Loading Matrix
DurationHrs | Fifty | SeventyFive | Ninety
1 | 212 | 196 | 182
2 | 179 | 168 | 157
4 | 150 | 144 | 136
6 | 134 | 131 | 126
8 | 128 | 125 | 121
12 | 122 | 119 | 117
16 | 117 | 115 | 113
20 | 113 | 111 | 110
24 | 108 | 107 | 107
Actual Loading Precentage > Equivalent Continous Pre-Load
We are undersized
What's the next size?
300 kVa | 151.6% | Still too high, over 119%
500 kVa | 90.99% | Just right
Customer eed 500 kVA transformer here
Transformer Ratings (kVA)
Single Phase |  | Three Phase
1 |  | 45
10 |  | 75
15 |  | 112.5
25 |  | 150
37.5 |  | 225
50 |  | 300
75 |  | 500
100 |  | 750
167 |  | 1000
250 |  | 1500
333 |  | 2000
500 |  | 2500
3750
5000
7500
10000

## OH65566592004-B
Reviewing to see if pre and post load duration makes a different if I move 12 hours in both directions from the highest peak instead of the peak load shape
| ReadDate | kVAReadValue | kWValue | KVARating | kVaSqaured | ActualLoadPercentage | OverRating
1 | 2018-02-12 19:00 | 110.666 | 99.6 | 225 | 12246.9636 | 202.1911 | 0
2 | 2018-02-12 20:00 | 97.066 | 87.36 | 225 | 9421.8084 | 202.1911 | 0
3 | 2018-02-12 21:00 | 104 | 93.6 | 225 | 10816 | 202.1911 | 0
4 | 2018-02-12 22:00 | 104.8 | 94.32 | 225 | 10983.04 | 202.1911 | 0
5 | 2018-02-12 23:00 | 132.533 | 119.28 | 225 | 17564.9961 | 202.1911 | 0
6 | 2018-02-13 | 110.133 | 99.12 | 225 | 12129.2777 | 202.1911 | 0
7 | 2018-02-13 01:00 | 112.266 | 101.04 | 225 | 12603.6548 | 202.1911 | 0
8 | 2018-02-13 02:00 | 108.266 | 97.44 | 225 | 11721.5268 | 202.1911 | 0
9 | 2018-02-13 03:00 | 128.8 | 115.92 | 225 | 16589.44 | 202.1911 | 0
10 | 2018-02-13 04:00 | 119.2 | 107.28 | 225 | 14208.64 | 202.1911 | 0
11 | 2018-02-13 05:00 | 134.133 | 120.72 | 225 | 17991.6617 | 202.1911 | 0
12 | 2018-02-13 06:00 | 165.6 | 149.04 | 225 | 27423.36 | 202.1911 | 0
| 2018-02-13 07:00 | 454.933 | 409.44 | 225 | 206964.0345 | 202.1911 | 1 | 1
1 | 2018-02-13 08:00 | 453.333 | 408 | 225 | 205510.8089 | 202.1911 | 1 | 2
2 | 2018-02-13 09:00 | 439.2 | 395.28 | 225 | 192896.64 | 202.1911 | 1 | 3
3 | 2018-02-13 10:00 | 326.933 | 294.24 | 225 | 106885.1865 | 202.1911 | 1 | 4
4 | 2018-02-13 11:00 | 285.866 | 257.28 | 225 | 81719.37 | 202.1911 | 1 | 5
5 | 2018-02-13 12:00 | 290.133 | 261.12 | 225 | 84177.1577 | 202.1911 | 1 | 6
6 | 2018-02-13 13:00 | 288.266 | 259.44 | 225 | 83097.2868 | 202.1911 | 1 | 7
7 | 2018-02-13 14:00 | 292.8 | 263.52 | 225 | 85731.84 | 202.1911 | 1 | 8
8 | 2018-02-13 15:00 | 289.866 | 260.88 | 225 | 84022.298 | 202.1911 | 1 | 9
9 | 2018-02-13 16:00 | 268 | 241.2 | 225 | 71824 | 202.1911 | 1 | 10
10 | 2018-02-13 17:00 | 268.266 | 241.44 | 225 | 71966.6468 | 202.1911 | 1 | 11
11 | 2018-02-13 18:00 | 152.8 | 137.52 | 225 | 23347.84 | 202.1911 | 0
12 | 2018-02-13 19:00 | 166.666 | 150 | 225 | 27777.5556 | 202.1911 | 0
11 Hours Above the kVa Rating so this equates to 12 hours
Actual Loading Percentage |  |  | 202.1924
Equivalent Pre Loading Calculation |  |  | 120.3122
Equivalent Post Loading Calculation |  |  | 305.3627
Pre Loading Condition Test Value |  |  | 135.7168 | Yeilds | 90 Percent | ??????
Ambient TempF |  | 86 |  | No Temperature Data Available set to 86 as default
Ambient TempC |  | 30
Allowable Loading Matrix
DurationHrs | Fifty | SeventyFive | Ninety
1 | 212 | 196 | 182
2 | 179 | 168 | 157
4 | 150 | 144 | 136
6 | 134 | 131 | 126
8 | 128 | 125 | 121
12 | 122 | 119 | 117
16 | 117 | 115 | 113
20 | 113 | 111 | 110
24 | 108 | 107 | 107
Actual Loading Precentage > Equivalent Continous Pre-Load
We are undersized
What's the next size?
300 kVa | 151.6% | Still too high, over 119%
500 kVa | 90.99% | Just right
Transformer Ratings (kVA)
Single Phase |  | Three Phase
1 |  | 45
10 |  | 75
15 |  | 112.5
25 |  | 150
37.5 |  | 225
50 |  | 300
75 |  | 500
100 |  | 750
167 |  | 1000
250 |  | 1500
333 |  | 2000
500 |  | 2500
3750
5000
7500
10000

## OH65567491004
ReadDate | kVAReadValue | kWValue | KVARating | kVaSqaured | ActualLoadPercentage | OverRating |  | percent | line
2018-02-21 18:00 | 144.466 | 130.02 | 112 | 20870.4252 | 145.9554 | 1 | 12 | 129% | 100%
2018-02-21 19:00 | 107.066 | 96.36 | 112 | 11463.1284 | 145.9554 | 0 | 11 | 95.59% | 100%
2018-02-21 20:00 | 96.866 | 87.18 | 112 | 9383.022 | 145.9554 | 0 | 10 | 86.49% | 100%
2018-02-21 21:00 | 91.133 | 82.02 | 112 | 8305.2237 | 145.9554 | 0 | 9 | 81.37% | 100%
2018-02-21 22:00 | 87.4 | 78.66 | 112 | 7638.76 | 145.9554 | 0 | 8 | 78.04% | 100%
2018-02-21 23:00 | 89.8 | 80.82 | 112 | 8064.04 | 145.9554 | 0 | 7 | 80.18% | 100%
2018-02-22 | 93.133 | 83.82 | 112 | 8673.7557 | 145.9554 | 0 | 6 | 83.15% | 100%
2018-02-22 01:00 | 59.666 | 53.7 | 112 | 3560.0316 | 145.9554 | 0 | 5 | 53.27% | 100%
2018-02-22 02:00 | 62.133 | 55.92 | 112 | 3860.5097 | 145.9554 | 0 | 4 | 55.48% | 100%
2018-02-22 03:00 | 52.6 | 47.34 | 112 | 2766.76 | 145.9554 | 0 | 3 | 46.96% | 100%
2018-02-22 04:00 | 48.933 | 44.04 | 112 | 2394.4385 | 145.9554 | 0 | 2 | 43.69% | 100%
2018-02-22 05:00 | 73.466 | 66.12 | 112 | 5397.2532 | 145.9554 | 0 | 1 | 65.59% | 100%
2018-02-22 06:00 | 117.666 | 105.9 | 112 | 13845.2876 | 145.9554 | 1 | 1 | 105.1% | 100% | LoadDuration
2018-02-22 07:00 | 134.266 | 120.84 | 112 | 18027.3588 | 145.9554 | 1 | 2 | 119.9% | 100% | LoadDuration
2018-02-22 08:00 | 136.466 | 122.82 | 112 | 18622.9692 | 145.9554 | 1 | 3 | 121.8% | 100% | LoadDuration
2018-02-22 09:00 | 136 | 122.4 | 112 | 18496 | 145.9554 | 1 | 4 | 121.4% | 100% | LoadDuration
2018-02-22 10:00 | 136.866 | 123.18 | 112 | 18732.302 | 145.9554 | 1 | 5 | 122.2% | 100% | LoadDuration
2018-02-22 11:00 | 137.666 | 123.9 | 112 | 18951.9276 | 145.9554 | 1 | 6 | 122.9% | 100% | LoadDuration
2018-02-22 12:00 | 141.933 | 127.74 | 112 | 20144.9765 | 145.9554 | 1 | 7 | 126.7% | 100% | LoadDuration
2018-02-22 13:00 | 145.2 | 130.68 | 112 | 21083.04 | 145.9554 | 1 | 8 | 129.6% | 100% | LoadDuration
2018-02-22 14:00 | 147.933 | 133.14 | 112 | 21884.1725 | 145.9554 | 1 | 9 | 132.1% | 100% | LoadDuration
2018-02-22 15:00 | 160.266 | 144.24 | 112 | 25685.1908 | 145.9554 | 1 | 10 | 143.1% | 100% | LoadDuration
2018-02-22 16:00 | 162.8 | 146.52 | 112 | 26503.84 | 145.9554 | 1 | 11 | 145.4% | 100% | LoadDuration
2018-02-22 17:00 | 163.466 | 147.12 | 112 | 26721.1332 | 145.9554 | 1 | 12 | 146% | 100% | LoadDuration
2018-02-22 18:00 | 160.133 | 144.12 | 112 | 25642.5777 | 145.9554 | 1 | 13 | 143% | 100% | LoadDuration
2018-02-22 19:00 | 106.733 | 96.06 | 112 | 11391.9333 | 145.9554 | 0 |  | 95.3% | 100%
2018-02-22 20:00 | 82.6 | 74.34 | 112 | 6822.76 | 145.9554 | 0 |  | 73.75% | 100% |  | Transformer is Over Loaded (undersized)
2018-02-22 21:00 | 92.2 | 82.98 | 112 | 8500.84 | 145.9554 | 0 |  | 82.32% | 100% |  | Actual Loading Percentage of 145.9518 is over the Allowable Loading Matrix for 16 hours and 50% value of 117%.
2018-02-22 22:00 | 77.066 | 69.36 | 112 | 5939.1684 | 145.9554 | 0 |  | 68.81% | 100%
2018-02-22 23:00 | 96.4 | 86.76 | 112 | 9292.96 | 145.9554 | 0 |  | 86.07% | 100%
2018-02-23 | 72.533 | 65.28 | 112 | 5261.0361 | 145.9554 | 0 |  | 64.76% | 100%
2018-02-23 01:00 | 64.666 | 58.2 | 112 | 4181.6916 | 145.9554 | 0 |  | 57.74% | 100%
2018-02-23 02:00 | 61.066 | 54.96 | 112 | 3729.0564 | 145.9554 | 0 |  | 54.52% | 100%
2018-02-23 03:00 | 60.266 | 54.24 | 112 | 3631.9908 | 145.9554 | 0 |  | 53.81% | 100%
2018-02-23 04:00 | 48.8 | 43.92 | 112 | 2381.44 | 145.9554 | 0 |  | 43.57% | 100%
2018-02-23 05:00 | 74.733 | 67.26 | 112 | 5585.0213 | 145.9554 | 0 |  | 66.73% | 100%
2018-02-23 06:00 | 117.333 | 105.6 | 112 | 13767.0329 | 145.9554 | 1 |  | 104.8% | 100% |  | Allowable Loading Matrix
[11 empty] | DurationHrs | Fifty | SeventyFive | Ninety
13 Hours Above the kVa Rating so this equates to 12 or 16 Hours???? hours | [10 empty] | 1 | 212 | 196 | 182
[11 empty] | 2 | 179 | 168 | 157
[11 empty] | 4 | 150 | 144 | 136
Actual Loading Percentage |  |  | 145.9518 | [7 empty] | 6 | 134 | 131 | 126
[11 empty] | 8 | 128 | 125 | 121
Equivalent Pre Loading Calculation |  |  | 87.7389 | [7 empty] | 12 | 122 | 119 | 117
Equivalent Post Loading Calculation |  |  | 81.8967 | [7 empty] | 16 | 117 | 115 | 113
[11 empty] | 20 | 113 | 111 | 110
Pre Loading Condition Test Value |  |  | 78.3383 | Yeilds | 90 Percent | [5 empty] | 24 | 108 | 107 | 107
Ambient TempF |  | 86 |  | No Temperature Data Available set to 86 as default
Ambient TempC |  | 30 | [8 empty] | Calculations
[11 empty] | Actual Loading Percentage |  |  | 145.9518
Allowable Loading Matrix
DurationHrs | Fifty | SeventyFive | Ninety | [7 empty] | Equivalent Pre Loading Calculation |  |  | 87.7389
1 | 212 | 196 | 182 | [7 empty] | Equivalent Post Loading Calculation |  |  | 81.8967
2 | 179 | 168 | 157
4 | 150 | 144 | 136 | [7 empty] | Pre Loading Condition Test Value |  |  | 78.3383 | Yeilds | 90 Percent
6 | 134 | 131 | 126
8 | 128 | 125 | 121 | [7 empty] | Ambient TempF |  | 86 |  | No Temperature Data Available set to 86 as default
12 | 122 | 119 | 117 | [7 empty] | Ambient TempC |  | 30
16 | 117 | 115 | 113
20 | 113 | 111 | 110
24 | 108 | 107 | 107
Actual Loading Precentage > Allowable Loading Matrix[]
We are undersized
What's the next size?
150 kVa | 109.6% | Just right
225 kVa | 73.05% | Just right
Transformer Ratings (kVA)
Single Phase |  | Three Phase
1 |  | 45
10 |  | 75
15 |  | 112.5
25 |  | 150
37.5 |  | 225
50 |  | 300
75 |  | 500
100 |  | 750
167 |  | 1000
250 |  | 1500
333 |  | 2000
500 |  | 2500
3750
5000
7500
10000

## OH64566256012
ReadDate | kVAReadValue | kWValue | KVARating | kVaSqaured | ActualLoadPercentage | OverRating | ReadLogDate
2018-01-31 07:00 | 1.871 | 1.684 | 10 | 3.5006 | 101.8 | 0 | 43131
2018-01-31 08:00 | 4.877 | 4.39 | 10 | 23.7851 | 101.8 | 0 | 43131
2018-01-31 09:00 | 5.235 | 4.712 | 10 | 27.4052 | 101.8 | 0 | 43131
2018-01-31 10:00 | 1.726 | 1.554 | 10 | 2.9791 | 101.8 | 0 | 43131
2018-01-31 11:00 | 1.186 | 1.068 | 10 | 1.4066 | 101.8 | 0 | 43131
2018-01-31 12:00 | 1.12 | 1.008 | 10 | 1.2544 | 101.8 | 0 | 43131
2018-01-31 13:00 | 1.255 | 1.13 | 10 | 1.575 | 101.8 | 0 | 43131
2018-01-31 14:00 | 1.771 | 1.594 | 10 | 3.1364 | 101.8 | 0 | 43131
2018-01-31 15:00 | 5.302 | 4.772 | 10 | 28.1112 | 101.8 | 0 | 43131
2018-01-31 16:00 | 3.746 | 3.372 | 10 | 14.0325 | 101.8 | 0 | 43131
2018-01-31 17:00 | 1.688 | 1.52 | 10 | 2.8493 | 101.8 | 0 | 43131
2018-01-31 18:00 | 6.04 | 5.436 | 10 | 36.4816 | 101.8 | 0 | 43131
2018-01-31 19:00 | 10.182 | 9.164 | 10 | 103.6731 | 101.8 | 1 | 43131
2018-01-31 20:00 | 4.735 | 4.262 | 10 | 22.4202 | 101.8 | 0 | 43131
2018-01-31 21:00 | 5.486 | 4.938 | 10 | 30.0962 | 101.8 | 0 | 43131
2018-01-31 22:00 | 2.102 | 1.892 | 10 | 4.4184 | 101.8 | 0 | 43131
2018-01-31 23:00 | 2.075 | 1.868 | 10 | 4.3056 | 101.8 | 0 | 43131
2018-02-01 | 1.713 | 1.542 | 10 | 2.9344 | 101.8 | 0 | 43131
2018-02-01 01:00 | 2.073 | 1.866 | 10 | 4.2973 | 101.8 | 0 | 43132
2018-02-01 02:00 | 1.468 | 1.322 | 10 | 2.155 | 101.8 | 0 | 43132
2018-02-01 03:00 | 1.415 | 1.274 | 10 | 2.0022 | 101.8 | 0 | 43132
2018-02-01 04:00 | 1.453 | 1.308 | 10 | 2.1112 | 101.8 | 0 | 43132
2018-02-01 05:00 | 1.406 | 1.266 | 10 | 1.9768 | 101.8 | 0 | 43132
2018-02-01 06:00 | 1.88 | 1.692 | 10 | 3.5344 | 101.8 | 0 | 43132
2018-02-01 07:00 | 1.882 | 1.694 | 10 | 3.5419 | 101.8 | 0 | 43132
13 Hours Above the kVa Rating so this equates to 12 or 16 Hours???? hours
Actual Loading Percentage |  |  | 101.82
Equivalent Pre Loading Calculation |  |  | 3.4942
Equivalent Post Loading Calculation |  |  | 2.6425
Pre Loading Condition Test Value |  |  | 1.553 | Yeilds | 50 Percent
Ambient TempF |  | 86 |  | No Temperature Data Available set to 86 as default
Ambient TempC |  | 30
Allowable Loading Matrix
DurationHrs | Fifty | SeventyFive | Ninety
1 | 212 | 196 | 182
2 | 179 | 168 | 157
4 | 150 | 144 | 136
6 | 134 | 131 | 126
8 | 128 | 125 | 121
12 | 122 | 119 | 117
16 | 117 | 115 | 113
20 | 113 | 111 | 110
24 | 108 | 107 | 107
Actual Loading Precentage < Equivalent Continous Pre-Load
We are fine
What's the next size?
1 | 1018%
10 | 101.8% | Just right
15 | 67.88%
Transformer Ratings (kVA)
Single Phase |  | Three Phase
1 |  | 45
10 |  | 75
15 |  | 112.5
25 |  | 150
37.5 |  | 225
50 |  | 300
75 |  | 500
100 |  | 750
167 |  | 1000
250 |  | 1500
333 |  | 2000
500 |  | 2500
3750
5000
7500
10000

## OH63572837010
ReadDate | kVAReadValue | kWValue | KVARating | kVaSqaured | ActualLoadPercentage | OverRating | ReadLogDate
2018-01-24 19:00 | 3.448 | 3.103 | 10 | 11.8887 | 1252.5 | 0 | 43124
2018-01-24 20:00 | 2.74 | 2.466 | 10 | 7.5076 | 1252.5 | 0 | 43124
2018-01-24 21:00 | 3.796 | 3.416 | 10 | 14.4096 | 1252.5 | 0 | 43124
2018-01-24 22:00 | 2.76 | 2.484 | 10 | 7.6176 | 1252.5 | 0 | 43124
2018-01-24 23:00 | 3.4 | 3.06 | 10 | 11.56 | 1252.5 | 0 | 43124
2018-01-25 | 3.016 | 2.714 | 10 | 9.0963 | 1252.5 | 0 | 43124
2018-01-25 01:00 | 3.112 | 2.8 | 10 | 9.6845 | 1252.5 | 0 | 43125
2018-01-25 02:00 | 3.396 | 3.056 | 10 | 11.5328 | 1252.5 | 0 | 43125
2018-01-25 03:00 | 2.988 | 2.689 | 10 | 8.9281 | 1252.5 | 0 | 43125
2018-01-25 04:00 | 3.16 | 2.844 | 10 | 9.9856 | 1252.5 | 0 | 43125
2018-01-25 05:00 | 2.996 | 2.696 | 10 | 8.976 | 1252.5 | 0 | 43125
2018-01-25 06:00 | 3.136 | 2.822 | 10 | 9.8345 | 1252.5 | 0 | 43125
2018-01-25 07:00 | 125.252 | 112.727 | 10 | 15688.0635 | 1252.5 | 1 | 43125
2018-01-25 08:00 | 119.2 | 107.28 | 10 | 14208.64 | 1252.5 | 1 | 43125
2018-01-25 09:00 | 5.961 | 5.365 | 10 | 35.5335 | 1252.5 | 0 | 43125
2018-01-25 10:00 | 1.392 | 1.252 | 10 | 1.9377 | 1252.5 | 0 | 43125
2018-01-25 11:00 | 1.628 | 1.465 | 10 | 2.6504 | 1252.5 | 0 | 43125
2018-01-25 12:00 | 1.24 | 1.116 | 10 | 1.5376 | 1252.5 | 0 | 43125
2018-01-25 13:00 | 1.396 | 1.256 | 10 | 1.9488 | 1252.5 | 0 | 43125
2018-01-25 14:00 | 1.288 | 1.159 | 10 | 1.6589 | 1252.5 | 0 | 43125
2018-01-25 15:00 | 1.352 | 1.216 | 10 | 1.8279 | 1252.5 | 0 | 43125
2018-01-25 16:00 | 1.396 | 1.256 | 10 | 1.9488 | 1252.5 | 0 | 43125
2018-01-25 17:00 | 3.52 | 3.168 | 10 | 12.3904 | 1252.5 | 0 | 43125
2018-01-25 18:00 | 2.964 | 2.667 | 10 | 8.7853 | 1252.5 | 0 | 43125
2018-01-25 19:00 | 3.196 | 2.876 | 10 | 10.2144 | 1252.5 | 0 | 43125
2018-01-25 20:00 | 3.208 | 2.887 | 10 | 10.2913 | 1252.5 | 0 | 43125

## OH66569034003
ReadDate | kVAReadValue | kWValue | KVARating | kVaSqaured | ActualLoadPercentage | OverRating
2018-02-13 07:00 | 15.653 | 14.088 | 25 | 245.0164 | 161.704 | 0
2018-02-13 08:00 | 14.68 | 13.212 | 25 | 215.5024 | 161.704 | 0
2018-02-13 09:00 | 20.72 | 18.648 | 25 | 429.3184 | 161.704 | 0
2018-02-13 10:00 | 22.066 | 19.86 | 25 | 486.9084 | 161.704 | 0
2018-02-13 11:00 | 23.173 | 20.856 | 25 | 536.9879 | 161.704 | 0
2018-02-13 12:00 | 21.826 | 19.644 | 25 | 476.3743 | 161.704 | 0
2018-02-13 13:00 | 23.08 | 20.772 | 25 | 532.6864 | 161.704 | 0
2018-02-13 14:00 | 21.2 | 19.08 | 25 | 449.44 | 161.704 | 0
2018-02-13 15:00 | 21.92 | 19.728 | 25 | 480.4864 | 161.704 | 0
2018-02-13 16:00 | 23.506 | 21.156 | 25 | 552.532 | 161.704 | 0
2018-02-13 17:00 | 23.973 | 21.576 | 25 | 574.7047 | 161.704 | 0
2018-02-13 18:00 | 23.76 | 21.384 | 25 | 564.5376 | 161.704 | 0
2018-02-13 19:00 | 40.426 | 36.384 | 25 | 1634.2615 | 161.704 | 1
2018-02-13 20:00 | 38.946 | 35.052 | 25 | 1516.7909 | 161.704 | 1
2018-02-13 21:00 | 39.76 | 35.784 | 25 | 1580.8576 | 161.704 | 1
2018-02-13 22:00 | 38.6 | 34.74 | 25 | 1489.96 | 161.704 | 1
2018-02-13 23:00 | 36.68 | 33.012 | 25 | 1345.4224 | 161.704 | 1
2018-02-14 | 34.84 | 31.356 | 25 | 1213.8256 | 161.704 | 1
2018-02-14 01:00 | 33.506 | 30.156 | 25 | 1122.652 | 161.704 | 1
2018-02-14 02:00 | 32.48 | 29.232 | 25 | 1054.9504 | 161.704 | 1
2018-02-14 03:00 | 16.626 | 14.964 | 25 | 276.4239 | 161.704 | 0
2018-02-14 04:00 | 13.32 | 11.988 | 25 | 177.4224 | 161.704 | 0
2018-02-14 05:00 | 14.88 | 13.392 | 25 | 221.4144 | 161.704 | 0
2018-02-14 06:00 | 13.546 | 12.192 | 25 | 183.4941 | 161.704 | 0
2018-02-14 07:00 | 14.133 | 12.72 | 25 | 199.7417 | 161.704 | 0
2018-02-14 08:00 | 11.186 | 10.068 | 25 | 125.1266 | 161.704 | 0
2018-02-14 09:00 | 20.453 | 18.408 | 25 | 418.3252 | 161.704 | 0
2018-02-14 10:00 | 18.893 | 17.004 | 25 | 356.9454 | 161.704 | 0
2018-02-14 11:00 | 22.16 | 19.944 | 25 | 491.0656 | 161.704 | 0
2018-02-14 12:00 | 20.84 | 18.756 | 25 | 434.3056 | 161.704 | 0
2018-02-14 13:00 | 20.826 | 18.744 | 25 | 433.7223 | 161.704 | 0
2018-02-14 14:00 | 24.44 | 21.996 | 25 | 597.3136 | 161.704 | 0
ReadDate | kVAReadValue | Percentage | EqLoadCycle |  |  |  | This chart
2018-02-13 07:00 | 15.653 | 62.61% |  |  |  |  | replicates what we
2018-02-13 08:00 | 14.68 | 58.72% |  |  |  |  | see in the IEEE document
2018-02-13 09:00 | 20.72 | 82.88%
2018-02-13 10:00 | 22.066 | 88.26% |  |  |  |  | Initial Load around 96%
2018-02-13 11:00 | 23.173 | 92.69% |  |  |  |  | Peak at 160
2018-02-13 12:00 | 21.826 | 87.3%
2018-02-13 13:00 | 23.08 | 92.32%
2018-02-13 14:00 | 21.2 | 84.8%
2018-02-13 15:00 | 21.92 | 87.68% |  |  |  |  | Things we need to display
2018-02-13 16:00 | 23.506 | 94.02%
2018-02-13 17:00 | 23.973 | 95.89%
2018-02-13 18:00 | 23.76 | 95.04%
2018-02-13 19:00 | 40.426 | 161.7% |  |  |  |  | Dashed Line should represent the
2018-02-13 20:00 | 38.946 | 155.8% |  |  |  |  | equivalent load cycle generated
2018-02-13 21:00 | 39.76 | 159% |  |  |  |  | from the action load cycle
2018-02-13 22:00 | 38.6 | 154.4%
2018-02-13 23:00 | 36.68 | 146.7% |  |  |  |  | 25.2602
2018-02-14 | 34.84 | 139.4%
2018-02-14 01:00 | 33.506 | 134% |  |  |  |  | This seems wrong here based on
2018-02-14 02:00 | 32.48 | 129.9% |  |  |  |  | the IEEE Document statements
2018-02-14 03:00 | 16.626 | 66.5% |  |  |  |  | what did I do wrong or interpret incorrectly???
2018-02-14 04:00 | 13.32 | 53.28%
2018-02-14 05:00 | 14.88 | 59.52%
2018-02-14 06:00 | 13.546 | 54.18%
2018-02-14 07:00 | 14.133 | 56.53%
2018-02-14 08:00 | 11.186 | 44.74%
2018-02-14 09:00 | 20.453 | 81.81%
2018-02-14 10:00 | 18.893 | 75.57%
2018-02-14 11:00 | 22.16 | 88.64%
2018-02-14 12:00 | 20.84 | 83.36%
2018-02-14 13:00 | 20.826 | 83.3%
2018-02-14 14:00 | 24.44 | 97.76%